## Slide 1
SKAO Power Update
2015 Engineering Meeting: Penticton
Adriaan Schutte
2015-11-11

## Slide 2
Power Restrictions on Sites
Consumption Management
  General budgeting procedure
  Power budgeting
  Power Maturity Levels (PMLs) & milestones
  Power allocations
Power Quality Standard
Overview

## Slide 3
SA: 4MW available (transient effects)
Power Restrictions

## Slide 4
Aus: Primarily diesel-based, high cost
Power Restrictions

## Slide 5
General Budgeting Process:
Consumption Management

## Slide 6
General Budgeting Process:
Consumption Management

## Slide 7
Tailored to power management
Include:
  Reticulation as loads
  Supply cost
  Operational budget
Consumption Management

## Slide 8
Power Maturity Levels (PMLs)
  Based on Technology Readiness Levels (TRLs)
  Evidence required (same data as for simulation)
Consumption Management
PML Required | PML Evidence Required | Milestone
1 | Power estimates based on first order calculations | 
2 | Estimates based on engineering analysis and simulation | Preliminary Design Review (PDR)
3 | Measurements in laboratory environment on test setups | PDR +9 Months
4 | Measurements in laboratory environment on breadboards | CDR -6 Months
5 | Measurements in a representative environment + PQ | Critical Design Review (CDR)
6 | Short term measurements + PQ on prototype for all operating scenarios | Production Readiness Review
7 | Medium term measurements +PQ on prototype for all operating scenarios | Before Site Testing is Allowed
8 | Medium term measurements on at least one production unit at site | Before Site Operation is Allowed
9 | Long term measurement on multiple production units | Completion of Commissioning

## Slide 9
Reporting in detail design phase:
  Revised power reporting document issued
  Implement PMLs
    “Engineering estimates” no longer OK
    Require simulations and then measurements
  Implement time-domain simulation
    Require power models from Consortia
    Consumption per science use case (Day in the Life)
    Identify other effects:
      Modes
      Temperature (e.g. cooling systems)
      Wind (e.g. dishes)
      Etc.
Consumption Management

## Slide 10
Recap: baseline v2 allocations SKA1 Low:
When running on diesel: 12,000 litres / day
Consumption Management
Element | Average & Peak Power Consumption (kW)
LFAA | 1,064
CSP Low Imaging | 30
CSP Low Non-Imaging | 144
TM Low | 20
SADT Low | 50
INFRA-AUS (LFAA) | 15
Cooling & Site Dist. Losses (INFRA) | 741
SKA1 LOW TOTAL | 2,062

## Slide 11
Recap: baseline v2 allocations SKA1 Mid:
When running on diesel: 30,000 litres / day
Consumption Management
Element | Average Power Consumption (kW) | Peak Power Consumption (kW)
Karoo Site Complex (incl. DRUPS, sheds, etc) | 380 | 530
Existing Equipment (KAT-7, etc). | 45 | 56
MeerKAT Dishes (64) | 864 | 1024
SKA1 Mid Dishes (133) | 1,130 | 1,530
CSP Mid Imaging | 170 | 170
CSP Mid Non-imaging | 420 | 420
TM Mid | 20 | 20
SADT Mid | 110 | 110
Cooling & Site Distribution Losses (INFRA-SA) | 867 | 1005
SKA1 MID SITE TOTAL | 4,007 | 4,865
33kV Line Losses | 450 | 690
Klerefontein Support Base | 25 | 45
Carnarvon POP Station | 5 | 10
SKA1 MID KAROO TOTAL | 4,487 | 5,610

## Slide 12
Operational cost (approx.):
  SKA1 Mid: Eur 7.5 mil / year (grid only)
  SKA1 Low: Eur 8 mil / year
Power cost is about 25% of annual budget
  Assuming ops budget is 10% of Eur 650 mil
  Assumptions on SDP consumption
Power Budget

## Slide 13
SKA PQ standard developed by INFRAs
Replace PQ sections in all ICDs
Based on international standards
Checked against ALMA and E-ELT standards
Status:
  In final review
  To be issued very shortly
Power Quality

## Slide 14
Thank You
Questions?